Standard Operating Procedure

for work with

| Chemical name/class: |  |  |  | Toxic Gases (customization required for PHS gases – must complete red sections) | CAS #: | Various |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PI: | All Duke PIs (customization required for PHS gases) |  |  |  | Date: |  |  |
| Building: |  | All Duke Buildings (customization required for PHSs) |  |  | Room #: |  |  |
|  |  |  | Designated Work Area for PHS gases: |  |  |  |  |

This SOP has been approved by the following Principal Investigator:

| Name: |  | Signature: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

- Circumstances of Use:

This SOP must be customized for each lab using toxic gases. A toxic gas is any gas on the particularly hazardous substances list and/or any gas with an NFPA health rating of 4. For toxic gases on the PHS list, you must list circumstances of use, including concentration and quantity.

- Potential Hazards:

Check the PHS list and Safety Data Sheet (SDS) to determine if the gas is a toxic gas. Consult the SDS for additional hazard information. All toxic gases will be supplied in compressed gas cylinders, and the SOP compressed gases must be followed. Some toxic gases will also be flammable, pyrophoric, or water reactive – in those cases, the SOPs for those physical hazards must also be followed. For toxic gases on the list of Particularly Hazardous Substances (PHSs), this section must indicate that the chemical is a PHS and why, and give a general overview of the hazards. If PHS gases have other hazards associated with their use (e.g. flammable, corrosive), those must also be addressed in this SOP. Alternately, this document may refer to another source of information (such as a lab inventory that includes basic hazard information).

- Engineering Controls:

The minimum acceptable engineering control for toxic gas use is a chemical fume hood. (One exception to this rule is diagnostic or therapeutic use of nitric oxide (NO), where the concentration of the gas in the cylinder is such that it does not pose a threat to human health.) Depending on the amount, concentration, and other properties of the gas, some of the following controls may be required: - Exhausted gas cabinets for cylinders and manifolds, possibly with air flow monitors and alarms - Toxic gas sensors and alarms - Restrictive flow orifices that limit the flow of gas - Secure storage - Gas scrubbing for exhaust

- Work Practice Controls:

- Specific written procedures, approved in advance by the Principal Investigator and OESO (as a High Risk Procedure), are required. These must cover all sections of this template. (OESO approval is not needed for diagnostic or therapeutic use of nitric oxide (NO) where the concentration of gas in the cylinder is below 25 ppm, but a written procedure is still needed.) - Purchase toxic gases in the lowest concentration and in the smallest cylinder that makes sense for the lab. - Check all fittings for leaks. - Keep valve closed and valve cover in place when gas is not in use. - Gas outlet must be inside chemical fume hood or other engineering control device. - All compressed gas cylinders shall be legibly marked by stenciling or stamping with at least the chemical name or commonly accepted name of the material contained. In addition, cylinders should bear the approved markings of the Department of Transportation stamped in the metal at the top of the cylinder.

- Personal protective equipment (PPE):

Engineering controls will provide the primary means of minimizing employee exposure to toxic gases, but in some cases emergency respirators may be advised. Contact OESO Occupational Hygiene and Safety at 919-684-5996 for advice on respiratory protection. As with all lab work, wear a fully buttoned lab coat, safety glasses, standard nitrile laboratory gloves, clothing covering the legs, and closed-toed shoes.

- Transportation and Storage:

- Cylinders (full or empty) shall be secured by chains, straps, or other sturdy tiedowns during storage and transport. - Cylinders shall be grouped by type of gas and the groups segregated as to compatibility. - Full cylinders shall be separated from empty cylinders within the storage area. - Flammable gases shall be separated from nonflammable gases. - Cylinders shall not be stored at temperatures above 125 F or in direct sunlight, or outside of the temperature range specified by the manufacturer. - Cylinder valves shall be kept closed when not in use. - Removable caps shall be kept on cylinders at all times, except when cylinders are in use. - Cylinders shall be protected against tampering and damage. - Cylinders shall not be stored near combustible materials. - Cylinders shall not be refilled. - Cylinders shall not be used or stored in cold rooms or other unventilated enclosures. An exception may be approved by OESO for inert gases when an oxygen monitor is in place.

- Waste Disposal:

In most cases, the compressed gas cylinder, including any unused gas, will be returned to the vendor from which the cylinder was purchased. If the vendor cannot be determined, contact OESO Environmental Programs at 919-684-2794 for information on disposal. OESO Environmental Programs should also be contacted to determine if the gas can be exhausted or if scrubbers are needed.

- Exposures/Unintended contact:

Contact Employee Occupational Health and Wellness (EOHW) at 919-684-3136 for medical advice on occupational chemical exposures. For an actual chemical exposure - Remove all persons from the contaminated area. (It may be necessary to go outside). - Call 911 from a campus phone or 919-684-2444 from any phone to request assistance if needed. Contact Employee Occupational Health and Wellness at 919-684-8115 for exposure-related advice. The work-related injury or illness report found at: http://www.hr.duke.edu/benefits/medical/workcomp/report.php should be completed within 24 hours. Follow-up medical attention should be sought through Duke Employee Occupational Health and Wellness (919-684-3136).

- Emergency/Release Procedure:

On the Durham campus, any uncontained release of toxic gases must be referred to the OESO spill response team by calling 911 from a campus phone or 919-684-2444 from any phone.

- Training of personnel:

All personnel are required to complete the online General Lab Safety session thru the OESO website. This session includes an introduction to general chemical safety. Furthermore, training on lab-specific procedures must be performed by the PI or knowledgeable designee for all personnel working with toxic gases, and must be documented (topics covered date, employee names and signatures). All personnel shall read and fully adhere to the laboratory- and chemical-specific SOP for each toxic gas, and shall document that they have read it by signing and dating the SOP.

“I have read and understand this SOP. I agree to fully adhere to its requirements.”

| Last | First | Duke ID | Signature | Date |
| --- | --- | --- | --- | --- |